Participants: Carolina Rodriguez; Thomas Williams; Jim Shearouse; Frederick Mill; Kim Holcomb; Paul H. Schmid

Weather condition: 40’s and rainy

Findings:

- Unsecure Doors:

  - Door #8:  Students entered door to go to breakfast.  Once entered the door was not locked; thus access to anyone from outside.  Not secured at 9:00 am nor when checked again at 9:15 am, subsequently door was locked.

- Corrective Action

- Doors will secured each day by 9:00 am

  - Door to cafeteria kitchen: in the process of the custodian taking out the trash the door was kept open, hence, providing access to anyone outside.

- Corrective Action

- Door will be secured at all times

- Stairway slipping hazard

  - Steps at door # 14 are used by students when entering the school.  Due to weather conditions, steps became wet and slippery.  While conducting the inspection a child slipped while climbing the steps.

- Corrective Action

- No response provided, no action taken.

- Improper Storage Practices

  - Dental hygienist room:  Old paper art supplies were staged improperly in front of the breaker boxes and sub panel; it impeded access to the breakers.

- Corrective Action

- Supplies moved and access to breaker cleared.  Main fuse box needs door and no action taken.

  - Clutter at entrance of Library

- Corrective Action

- Library does not have enough storage room, hence; for the materials right outside the door.  Materials are out of traffic area and it is not causing a safety issue.

  - Clutter discovered in a lot of different areas.

- Corrective Action

- Custodians surveyed the areas and clutter was properly cleaned up

- Transportation

  - Busses arrive 15 minutes early to the required location. Children receiving breakfast go into the building; however, those not eating breakfast sit on the bus until it is time to enter the school.  During that time busses stay idling for about 15 minutes.

- Bus drivers were not observed inspecting the bus prior to leaving the school.  As per the Supervisor of Transportation, employees inspect bus back at the central location.

- Corrective Action

- Buses idle time depends on the weather.  Some of the drivers always walk through the bus before leaving the school, it is mandatory.

- Electrical Issues:

  - Extension cords are used throughout the building due to the lack of outlets.

    - These extension cords were not in use but still plugged into the outlets

    - Some were stored under boxes

    - One was under a water fountain (Ms Dailey’s hallway)

- Corrective Action

- Infrastructure will be updated or improved next year with QZAB for technological upgrades.

  - GFI at library

    - No GFI on two receptacles by sink in library office

- Corrective Action

- GFI has been installed.

  - Electrical circuit breaker boxes  (Library and Miss Weseloh’s room)

    - Circuit breaker box was found unlocked (library had key attached)

    - Library panel had missing circuit breaker…panel B # 21 uncovered

    - Miss Weseloh’s  room had a missing outlet cover  located over sink

    - Computer room had all outlets for computers floor mounted

    - Guidance office had an exposed wire by the teacher’s desk

- Corrective Action

- Employees were made aware that boxes should be closed, however; they shouldn’t be locked due to emergency circumstances. Exposed wire by teacher’s desk has been corrected.  Electrical upgrades will be conducted with QZAB.

- Noted Unsafe conditions:

  - Miss Weseloh’s room door entrance molding was unlevel and unattached

- Corrective Action

- Door entrance molding is attached.

  - Radiator heater was too close to one computer station causing a potential burn incident

- Recommendation

- Computer station should be moved away from the radiator.

  - Bathroom by nurse’s station, had radiator heater adjacent to urinal. Access to urinal required the user to slide into space

- Corrective Action

- No corrective action taken at this time. Cost analysis needs to be done, in order to remove radiator heater.

  - Bathroom across from Miss Weseloh’s class light fixture cover was coming off

- Corrective Action

- Light has been fixed.

  - Radiator heaters are not properly covered, which could potentially burn the child or adult

- Corrective Action

- No action taken.

  - Debris found in return vent in room #24

- Corrective Action

- Vent has been properly cleaned

  - Chemicals stored improperly in cafeteria kitchen above the freezer

- Corrective Action

- Corrected on the spot by a custodian. Employees were made aware not to store chemicals above food items.

  - Storeroom in cafeteria kitchen very cluttered and disorganized

- Corrective Action

- Corrected on Feb 28, misc clutter was removed from stored room, shelves were organized.

  - Window in library does not close, there is an inch gap

- Corrective Action

- Window has been properly secured.

  - Boiler room unsecured, hence access to anyone in the vicinity

- Corrective Action

- Door will be closed and secured.

  - Elevator did not have phones available

- Corrective Action

- Corrective action could not be taken at this point in time.

  - Walking surfaces outside of building are uneven and hazardous

- Corrective Action

- Some of the hazardous issues will be addressed with the upgrade.

  - Emergency evacuation routes were not posted in each room and hallway

- Corrective Action

- No corrective action taken.

  - Ceiling tiles by main entrance (car rider area) are not properly set

- Corrective Action

- Ceiling tiles were fixed and replaced.

  - Conference room ceiling tile was coming down

- Corrective Action

- Frame work has been fixed, and ceiling time has been properly fixed.

  - Fixed ladders not equipped with side cages, rails, landing or special fall protection

- Corrective Action

- Side cages are not needed as per code.

  - An antiquated and unsafe floor fan, held together by string and wire was housed on a chair and a box near the window at the far end of the library

- Corrective Action

- No corrective action taken.

- Other observations:

  - Lights in rooms do not automatically shut off when no one is present or the room is not in use, i.e. bathrooms, Mr. Wagner’s room and computer room.

- Corrective Action

- Lights will be upgraded with QZAB.

  - Computer room was not locked;  however, all computers did have combination locks  and were secured to the desks

- Corrective Action

- Computer room could not be locked at this point in time, will be fixed with upgrades done to buildings.

  - No AED in nurse’s office

- Recommendation

- AED should be located in the nurse’s office.

  - The nurse’s office does not have a segregated area for sick children

- Corrective Action

- No corrective action could be taken at this point in time.

  - Room # 40 radiators were blocked, obstructing the heat from circulating

- Corrective Action

- Item blocking the radiators were removed.